## Slide 1
Technical discussion today, identifying selection factors and hydrogeology
No final site is selected or recommended at this time
Environmental review with multiple alternatives
Staff recommends final site
Final property purchase after environmental review
Coast Development Permit process
Program C Well Site Selection
Process

## Slide 2
No assumptions on willingness of sellers
Other sites may be identified and pursued
Other factors or criteria may be identified
Program C Well Site Selection

## Slide 3
Site A – Adjacent to LOMS Play Fields
Site B – Private Property on Sage Avenue
Site C – Private Property on Andre Avenue
Site D – Vacant Area South of Sunny Oaks MHP
Los Osos Valley Road
South Bay Blvd
Los Osos Creek

## Slide 4
Site A – Adjacent to LOMS Play Fields
Site B – Private Property on Sage Avenue

## Slide 5
Site C – Private Property on Andre Avenue
Andre Avenue

## Slide 6
Site D – Vacant Area South of Sunny Oaks MHP
Los Osos Valley Road

## Slide 7
Basin Cross Section
Notes: Ray Dienzo
LOCSD =634 AF
GSWC = 564 AF
ST= 48 AF

## Slide 8
Notes: Ray Dienzo
LOCSD =634 AF
GSWC = 564 AF
ST= 48 AF

## Slide 9
Basin Cross Section – Looking East
Notes: Ray Dienzo
LOCSD =634 AF
GSWC = 564 AF
ST= 48 AF

## Slide 10
Site A – LOMS (Zone D/E): Key concern, disadvantage – perhaps < 100 AFY
Site B – Sage (Zone D/E): Concern, disadvantage – perhaps < 100 AFY
Site C – Andre (Zone D/E): Deepest portion of Zones D & E, advantage, >140 AFY
Site D – Sunny Oaks (Zone C/D/E) – good production including Zone C, advantage
>190 AFY
Annual Production

## Slide 11
Site A – LOMS: 1,100’ pipeline required, neutral
Site B – Sage: 2,200’ pipeline required, disadvantage
Site C – Andre: 600’ pipeline required, advantage
Site D – Sunny Oaks: 1,200 ‘ pipeline required using trenchless technology, neutral
Proximity to Infrastructure
(Community Water Mains)

## Slide 12
Site A – LOMS: Expected to be non-controversial - advantage
Site B – Sage: Potential controversy, disadvantage
Site C – Andre: Significant community concern - disadvantage
Site D – Sunny Oaks: Neighborhood opinion unknown at this time
Neighborhood/Community
Acceptance

## Slide 13
Site A – LOMS: Advantage
Site B – Sage: Unknown, premature
Site C – Andre: Advantage
Site D – Sunny Oaks: Unknown, premature
Seller Status and Land Cost

## Slide 14
Site A – LOMS: Advantage – not in residential neighborhood
Site B – Sage: On large residential parcel - mitigation required including submersible pump and sound proof enclosure
Site C – Andre: 1-acre lot in residential neighborhood – mitigation required including submersible pump and sound proof enclosure
Site D – Sunny Oaks: adjacent to mobile homes - mitigation required including submersible pump and sound proof enclosure
Aesthetic Concerns
Noise, Visual, other

## Slide 15
Example well site
Well piping and controls will be enclosed in building
No above ground motor – submersible proposed for all sites

## Slide 16
Use of site as corporation yard not anticipated – Example from LOCSD South Bay Well

## Slide 17
Example well sites – Palisades Well
Well in enclosure/building
Library building

## Slide 18
Site A – LOMS: Advantage – no residential wells in vicinity
Site B – Sage: Minor or negligible impacts to existing residential wells expected, mitigation may be required in environmental document
Site C – Andre: Minor or negligible impacts to existing residential wells expected, mitigation may be required in environmental document
Site D – Sunny Oaks: Advantage – no residential wells in vicinity
Potential interference with
Surrounding wells

## Slide 19
Potential Site C Well
Existing upper aquifer well in blue
Existing mixed aquifer well in pink
Existing perched aquifer well in green

## Slide 21
Initial technical study to be released via web after review of draft
Impacts must be mitigated if site selected
Modeled impacts are range from 4’ to 6’ at full 200 acre ft per year production
Even with these small draw down levels, some impacts may require mitigation in wells adjacent to Site C
If pursued, additional field testing and discussion of specific mitigations will be recommended
Potential interference with
Surrounding wells – Site C

## Slide 22
Modeled interference in upper aquifer wells

## Slide 23
Modeled interference in mixed aquifer wells

## Slide 24
Site A – LOMS: Advantage – developed area
Site B – Sage: Disadvantage – undeveloped with potential habitat
Site C – Andre: Advantage - developed
Site D – Sunny Oaks: Disadvantage – undeveloped with potential habitat
Environmental and Endangered
Species Impacts

## Slide 25
Site A – LOMS: Advantage with some constraints
Site B – Sage: Advantage
Site C – Andre: Disadvantage, but feasible
Site D – Sunny Oaks: Advantage
Site Layout and Access

## Slide 26
Site A – LOMS: Advantage – developed, non-controversial site
Site B – Sage: Disadvantage – undeveloped habitat with potential neighborhood concerns
Site C – Andre: Disadvantage – neighborhood concerns
Site D – Sunny Oaks: Disadvantage – undeveloped habitat with potential neighborhood concerns
Environmental and
Coastal Development Permit Timing